## STEAM FLOW MEASUREMENT SPECIFICATION

## Mass Flow Meter for Saturated Steam 			 		  July 2013

Furnish and install an ONICON F-2000 Series Vortex Mass Flow Meter complete with integral density compensation to provide direct mass steam flow output.  The flow meter shall calculate mass flow corrected for density with real time calculations based on temperature measured by an integral 1,000 ohm platinum RTD.  Mass flow inferred from specified steam pressure or calculated externally to the flow meter will not be acceptable.  The flow meter shall be sized by the manufacturer for each specific application and installed according to manufacturer’s recommendations. Provide a flow straightener, if required to meet the manufacturer’s minimum upstream straight pipe run requirement.  Provide lateral and horizontal supports as required to minimize vibration at the meter location.   Each individual flow meter shall undergo a multipoint point calibration against the manufacturer’s N.I.S.T. traceable flow standards.  The manufacturer shall provide a certificate of calibration for each meter.  The flow meter shall be programmed by the manufacturer for each specific application and shall be ready to use upon delivery.  Mass flow accuracy shall be within ± 1.5% of actual reading over the range of the meter, including all errors associated with velocity measurement, temperature and/or pressure measurement, and density compensation.  The meter shall be provided with ANSI class 150 or class 300 flanges as required to meet system requirements.  The maximum operating temperature shall be 5000 F. The flow meter body shall be constructed of 316L stainless steel and include a weather-tight NEMA-4X aluminum electronics enclosure. The meter shall display steam mass flow rate and mass flow total with an integral LCD display and support field programming of all parameters.  The meter shall also have integral diagnostics to verify installation conditions and the proper operation of the meter.  The meter shall provide a loop-powered 4-20 mA output signal calibrated in direct mass flow rate units for connection to the Central Control System.  In addition, an integral pulse output for steam mass flow totalization shall be provided.  All outputs shall be linear with mass flow rate.

Optional Remote Electronics Module:

Provide remote mount electronics option with 50 ft. factory cable and mounting bracket.

Optional Multi-analog Output Electronics Module:

Provide external 24VDC or 120VAC powered electronics that provides 3 analog (4-20mA) outputs capable of providing analog flow, temperature and pressure signals.

Optional Remote Auxiliary Display Module:

Provide an ONICON Model D-100 Display Module for remote LCD indication of Mass Flow Rate and Total Mass.  The indicators shall be housed in a wall mountable 8” x 10” x 4” steel NEMA-13 enclosure.  Output signals for mass flow rate (4-20 mA) and total (pulse) shall be available at the display module terminal strip, for connection to the Central Control System.  Provide 24 or 120 VAC input power to the display module (this version may not be loop-powered).  An internal 24VDC power supply shall provide power to the F-2600 Series Flow Meter.

Optional Remote Serial Network Interface Module:

Provide an ONICON D-100 with a serial communications interface. The network interface shall transmit Mass Flow Rate and Total Mass data via a serial interface conforming to one of the following protocols: BACnet MS/TP, BACnet IP, LONWORKS, MODBUS RTU RS485, MODBUS TCP/IP, JCI-N2 or Siemens P1.